OpenComms Network Interface Card (NIC)

DESCRIPTION	The OpenComms Network Interface Card provides Network and Modbus connectivity for your Emerson Network Power equipment.  Operating status is monitored and alarms are communicated via the network, using SNMP and/or HTTP protocols and over RS-485 using Modbus protocol.

DIMENSIONS:	Net:	178mm  x  102mm  x  38mm	0.2kg

7”  x  4”  x  1.5”	0.4lbs

As Shipped: 	229mm  x  140mm  x  64mm	0.6kg

9.0"  x  5.5"  x  2.5"	1.3lbs

POWER INPUT:	AC Input Voltage:	18VAC  to  24VAC

50/60 Hz, single phase

DC Input Voltage:	12VDC  to  36VDC

Power Consumption:	6VA maximum

ENVIRONMENT:	Operating Ambient Temperature:	5(C  to  40(C

41(F  to  104(F

Storage Ambient Temperature:	-20(C  to  60 (C

-4(F  to  140(F

Relative Humidity:	10%  to  90% RH, non-condensing

Communications:	Unit Input Communications:	2-Position Terminal Block

UPS Unit Input (not all):	20-Pin Vertical Header with Ejection Latches

Modbus In / Out:	2-Position Terminal Block

Network In / Out:	10baseT Ethernet Network:	RJ45 jack

SNMP v1, v2c with MIB-II support

HTTP 1.1

Telnet

BootP, DHCP per RFC2131/2132

Service Terminal (RS232):	DB9F, DTE

PROTECTION:	SELV Isolated User Connections

On-board Battery: minimum 100 hours of data and configuration retention

Watchdog Timer Circuitry

Manual Reset Pushbutton

COMPATIBILITY:

(All units are manufactured in North American unless otherwise noted)

Environmental Units with the following Microprocessors:

| Advanced Graphics (Deluxe Sys3, Challenger) | Advanced Micro (Deluxe Sys3, Challenger) |
| --- | --- |
| Standard Microprocessor (Deluxe Sys3, Challenger) | MiniMate II |
| Level 00 (Deluxe Sys3, Challenger) Level 10 (Deluxe Sys3, Challenger) Level 05/15 (UK) | HiMod |
| Emerson Network Power – Australia (CEMS100 / LECS15) |  |

3-Phase UPS:

| Npower | Hiross 7200 (Italy) |
| --- | --- |
|  | Hiross HiPulse (Italy) |

3-Phase Power:

| PDU and DataWave with PMP or EPMP monitoring | Static Switch |
| --- | --- |
|  | Static Switch 2 |

OVERALL AND MOUNTING DIMENSIONS:

CUSTOMER WIRING:

# Text boxes

Twisted-pair wires are recommended for:

- input from unit (TB1),

- Modbus output (TB2).

Note polarity as indicated.  Maximum cable run: 1000ft (328m) @ 22AWG.

24VAC power for the OpenComms Network card should be applied to TB3.  This input is not polarized.